## DD - Comment Session
Response of 100% SD comments tracker | NOT INCLUDED
Send the MEP (100% SD) comments impacting other disciplines like Arch/STR/ID to PM
Obtain FM comments
Obtain Multi-D comments
Obtain STR comments impacting MEP
Obtain ARCH comments
Obtain LNDS comments
Obtain LS comments
Obtain ID comments
Obtain Baseline program from PM for DD stage
Send the List of dependencies to PM (Refer 100% DD Dependencies Tab)

## DD - Submission
Calculation validation
Engrs to update AC calculations based on the above coordination
Engrs to update Ventilation calculations based on the above coordination
Engrs to update Smoke Ventilation calculations based on the above coordination
Engrs to update Fire fighting calculations based on the above coordination
Engrs to update Rainwater/Drainage calculations based on the above coordination
Engrs to update Irrigation/domestic water calculations based on the above coordination
Engrs to update EM ltg calculations based on the above coordination
Engrs to update FA calculations based on the above coordination
Engrs to update Busbar calculations based on the above coordination
Engrs to update Normal lighting calculations based on the above coordination
Engrs to update Voltage drop calculation based on the above coordination
Engrs to update Containment calculation based on the above coordination
100% DD Report
Identify any risks based on the progress during DD and append to the report
Engrs to update the latest bulk loads/equipment in the report
Engrs to update any strategies as applicable in the report
Issue the report to QA/QC team
Obtain QA/QC comments
Update the report based on QA/QC comments
Lead engr to review all the calculations
Engrs to update and upload to ACC submission folder
Outline specifications
Obtain the latest Abudhabi based specs from MLD team
Ensure all the authority specified product (transformer, QRM/TRM) specs are included
Identify any special requirement from the operator's guidelines and include in the respective sections
Issue the Specs to QA/QC team
Obtain QA/QC comments
Update the comments based on QA/QC comments
Engrs to upload all the specs to ACC submission folder
100% DD Calculations
Engrs to update all the calculations based on the above coordination
Issue the calculations to QA/QC team
Lead engr to review all the calculations
Obtain QA/QC comments
Update the calculations based on review
Engrs to update and upload all the calculations to ACC submission folder
100% SD Schematics
Engrs to review and update the schematics based on the above coordination & calculations
Modellers to update the schematics
Engrs to review the updated schematics
Lead engrs to review all the schematics
Update the schematics based on the review
Issue the schematics to QA/QC team
Obtain QA/QC comments
Update the calculations based on QA/QC comments
Modellers to update the model based on the comments, carry out interference check
BIM leads to verify all the comments are incorporated
Repeat the above steps until all the comments are closed
BIM leads to verify the final layouts and upload on the ACC submission folder
100% DD Layouts
Project BIM leads to verify all the layouts against TIDP
Project BIM leads to review the models & layouts and share it with BIM manager for further review
BIM leads / Modelers to share all the layouts with Engrs for review
Engrs to review all the layouts and provide comments
Modellers to update the model based on the comments, carry out interference check
BIM leads to verify all the comments are incorporated
Repeat the above steps until all the comments are closed
Modelers to share the final layouts with Engrs
Engrs to share the final layouts with MLD for QA/QC
Engrs to validate the comments from MLD, discuss with MLD QA/QC team and agree on the way forward
Engrs to provide the mark-up/information to the modelers to update the models
Modellers to update the model based on the comments, carry out interference check
BIM leads to verify all the comments are incorporated
Repeat the above steps until all the comments are closed
BIM leads to verify the final layouts and upload on the ACC submission folder

## DD - HVAC Detailed Design
Air Conditioning System - this activity shall be repeated floor-wise/apartment-wise
Obtain Window to Wall ratio from arch
Obtain U-values from arch
Carry out HAP calculation
Use HAPExt to generate FCU schedules
Obtain the grill locations from the coordinated RCP
Validate the grill size using HAP AirSizer
Obtain FCU selections from Vendors
Provide mark-ups/information to modelers for duct & chilled water routing
Modelers to use the chilled water routing plug-in for annotating the flowrates/sizes
Modelers to model all the ductworks and ensure that the flowrates are included within the family parameters (Flowrates should be updated automatically once flowrates are assigned to the grilles)
Modelers to generate duct quantity schedule having flowrates, velocities and pressure drop for engineers review
Engineers to review the layouts and duct schedules and provide comments
Modelers to incorporate the comments and finalise the layout
Air Conditioning System Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall AC & CHW schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics
Ventilation System - this activity shall be repeated floor-wise/apartment-wise
Obtain ventilation requirements for pool/water feature plantrooms
Obtain ventilation requirements for commercial kitchens, if any
Revise the ventilation calculation
Generate FAHU schedule
Obtain FAHU selection from Vendors
Provide mark-ups/information to modelers for duct routing
Modelers to model all the ductworks and ensure that the flowrates are included within the family parameters (Flowrates should be updated automatically once flowrates are assigned to the grilles)
Modelers to generate duct quantity schedule having flowrates, velocities and pressure drop for engineers review
Engineers to review the layouts and duct schedules and provide comments
Modelers to incorporate the comments and finalise the layout
Ventilation System Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall ventilation schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics

## DD - Electrical Detailed Design
Lighting & Small Power Layouts - Common Areas (For FOH areas, the modeling should commence after completing the RCP coordination) - this activity shall be repeated floor-wise
Obtain specialist lighting models including control schedules for FOH areas
Review the SD layouts and provide mark ups for additional lights - BOH area, where required and circuiting details
Review the SD layouts and provide mark ups for additional sockets, where required
Mech to provide location of FCU's/VAV's/MSFD's on the model as applicable - This item may take longer but this is a placeholder for tracking
PHE to provide location of Water heaters, Urinal sensors, etc on the model as applicable - This item may take longer but this is a placeholder for tracking
Populate all the equipment, sockets and issue the draft layout to engrs for circuiting
Engineers to complete the DB schedule
Engineers to issue the mark-up/load schedule to BIM for modelling
Modellers to complete the layout and issue check print to engineers
Engrs to review the layouts & provide comments
Modelers to incorporate the comments and finalise the layout
Lighting & Small Power Layouts - Apartement (For FOH areas, the modeling should commence after completing the RCP coordination) - this activity shall be repeated for every apartment
Obtain specialist lighting models including control schedules
Review the Coordinated ID RCP layout
Provide mark-ups for circuiting and switches
Obtain the SMP layout from ID
Obtain the white good's selection from ID
Align sockets and other power points as per the ID layout
Engineers to complete the DB schedule
Engineers to issue the mark-up/load schedule to BIM for modelling
Modellers to complete the layout and issue check print to engineers
Engrs to review the layouts & provide comments
Modelers to incorporate the comments and finalise the layout
LV Power Distribution - Layouts - this activity shall be repeated floor-wise
Mechanical/PHE to provide all the equipment loads
Engrs to obtain the loads for VT, BMU, ELV, Signage
Engr to update all the MCC/SMDB/LV Panel load schedules
Engr to update the Cable tray calculations
Engrs to provide mark-up/information to modelers for updating the models
Mech/PHE to update their models with the location of all equipment
Modellers to update the model as per the engr's mark-up & load schedules
Modellers to issue check print to engineers
Engineers to review & provide comments to modellers
Modelers to incorporate the comments and finalise the layout
Aircraft Warning Lights
Engineers to obtain the aeronautical survey report from the PM
Engrs to coordinate the location of lights with Façade consultants and architects
Engrs to provide mark-ups for lighting positions based on the coordination
Engrs to provide mark-ups for UPS/power supply information
BIM to incorporate all the comments as per mark-ups & issue check prints
Engr to reivew the revised check print
Modelers to incorporate the comments and finalise the layout
LV Power Distribution - Schematics
Mechanical/PHE to provide all the equipment loads
Engrs to obtain the loads for VT, BMU, ELV, Signage
Engr to update all the MCC/SMDB/LV Panel load schedules
Modeler to start preparing the schematics as per the updated load schedules
Modellers to issue check print to engineers
Engineers to review & provide comments to modellers
Modelers to incorporate the comments and finalise the schematics
Lightning Protection System & Earthing
Obtain the risk assesment report from atleast three vendors
Discuss with vendors about the requirement for intermediate ring conductors and obtain the installation details if required
Coordinate the location/details of intermediate ring conductor/strike pads with facade consultant
Incorporate the intermediate conductor/strike pads in the model
Indicate the air termination network on the roof and provide bonding to any metallic parts if advised by the vendor
Indicate the downconductor locations on the all the typical floor/GF/basement power layouts
Indicate test points on the columns on basement earthing/LPS layout
Review the earthing schematics and provide mark-ups if any change is required
Indicate the earth pits on basement layouts as per the schematics
Indicate looping conductors and cable tray/conduits for earthing cables from substation/LV rooms to earth pits in the basement
Issue check prints to Engr for review
Engineers to review & provide comments to modellers
Modelers to incorporate the comments and finalise the layout
Fire Alarm System and Emergency Lighting system - this activity shall be repeated floor-wise
BIM to update the location of devices as per the coordinated RCP
BIM to superimpose all the Mech/PHE equipment on FA/EM layouts and add IFU's (next to Access Panels) for the equipment
Engr to review the FA & EM lighting layouts and provide mark-up for any additional devices
Engr to propose cable tray route from FCC/CBS room upto the core & provide mark-ups
Review the schematics and provide mark-ups if any change is required
BIM to incorporate all the comments as per mark-ups & issue check prints
Engr to reivew the revised check print
Modelers to incorporate the comments and finalise the layout

## DD - BOH - Coordination
RCP (this item to be repeated floor-wise or area-wise) - validation only where this task has been completed in the SD stage
Arch to update their model with RCP
BIM to extract latest RCP layouts and Provide to Engineer for markups
Lighting calculation - BOH areas
EM ltg calculation - BOH areas
Provide mark-up for presence sensors/calculation output to BIM modellers
Provide mark-ups for fire alarm layouts
Arch to finalise the Air Outlet types
Provide mark-ups for grilles/diffusers
Provide mark-ups for FCU's/access panels
Water Heater calculation
Obtain Coordinated RCP layouts from BIM
Provide mark-ups for EWH location/access panels
Validate the Sprinkler Spacing/ IV's & Access Panels for water supply
Prepare models for the above and issue coordinated model to engineers for review
Update model based on the engineers' comments (if any) and issue coordinated model to Arch for RCP coordination
Obtain Arch Comments
Initiate MEP/Arch Coordination meeting to agree on Arch comments and any MEP requirements
BIM Team to update model as per comments
Wall Coordination (this item to be repeated floor-wise or area-wise)
MEP to finalise location of switches/sockets/MEP fixtures
MEP to finalise the thermostat location
Validate locations of smoke extract & make-up grilles
Update model based on the engineers' comments and issue coordinated model to Arch for coordination
Obtain Arch Comments
Initiate MEP/Arch Coordination meeting to agree on Arch comments and any MEP requirements
BIM Team to update model as per comments
Floor Coordination (this item to be repeated floor-wise or area-wise)
Populate floor trap locations matching Arch layout
Validate locations and Update model
Obtain Arch Comments
Initiate MEP/Arch Coordination meeting to agree on Arch comments and any MEP requirements
BIM Team to update model as per comments

## DD-ID - Coordination
RCP (this item to be repeated floor-wise or area-wise) - validation only where this task has been completed in the SD stage
ID to update their model with RCP having specialist lighting
BIM to extract latest RCP layouts and provide to Engineer for markups
EM ltg calculation - FOH areas
Provide mark-up for presence sensors/calculation output to BIM modellers
Provide mark-ups for fire alarm layouts
ID to finalise the Air Outlet types
Validate the grill size using HAP AirSizer
Provide mark-ups for grilles/diffusers
Provide mark-ups for FCU's/access panels
Water Heater calculation
Obtain Coordinated RCP layouts from BIM | -
Provide mark-ups for EWH location/access panels
Validate the Sprinkler Spacing/ IV's & Access Panels for water supply
Prepare models for the above and issue coordinated model to engineers for review
Update model based on the engineers' comments (if any) and issue coordinated model to ID for RCP coordination
Obtain ID Comments
Initiate MEP/ID Coordination meeting to agree on ID comments and any MEP requirements
BIM Team to update model as per comments
Wall Coordination (this item to be repeated floor-wise or area-wise)
Obtain the ID layout indicating location of switches/sockets/MEP fixtures
MEP to finalise the thermostat location
Validate locations of Emergency gas switch/ gas detector in model
Validate locations of smoke extract & make-up grilles
Populate locations of Gas meter, piping and accessories inside the cabinet
Update model based on the engineers' comments and issue coordinated model to ID for coordination
Obtain ID Comments
Initiate MEP/ID Coordination meeting to agree on ID comments and any MEP requirements
BIM Team to update model as per comments
Floor Coordination (this item to be repeated floor-wise or area-wise)
Populate floor trap locations matching ID layout
Validate locations and Update model
Obtain ID Comments
Initiate MEP/ID Coordination meeting to agree on ID comments and any MEP requirements
BIM Team to update model as per comments

## DD-Deliverable Setup
| Engrs to provide the List of Deliverables to BIM Manager | Shajjad - Its required for all stage - Will discuss in tomrorow call
BIM Manager to prepare the TIDP and share with Engrs for review
Engrs to review and provide feedback to BIM manager
BIM manager to finalise the TIDP and share with the team
Custom Requirement | BIM leads to upload the TIDP on ProManage tool and start tracking the progress

## DD-Space Planning
NO TASKS
Validate all the MEP space planning as per the comments received on 100% SD package
Issue comments/revised space planning to arch/ID
Obtain revised arch/ID layouts based on the above comments

## DD-Major Services Routing
Major Services Routing Validation | NOT INCLUDED
Infra tie-in points to Primary Plantrooms | NOT INCLUDED
HVAC
Validate/model CHW tie-in line upto the ETS room
Validate/mark the STR opening for CHW tie-in and share with STR
Obtain feedback from STR and modify the route if required
Ensure the openings are reflected in the STR model
Elect
Review the 11kV tie-in connections to the substations (RMU+Tx s/s only)
Coordinate with Landscape & STR for including the T-T trenches, if not provided already
Validate the 11kV cable routes in the basement - ensure there are no services running in parallel; Bottom of tray should be at 2400AFFL; Allow for 1200 from atleast one side for clear access; Allow for min 400 above the tray from any services/soffit
Validate all the LV cable tray routes within the basement/GF
Validate all the tray risers
Validate tray/trunking routing on the typical floors
Main trays all change to ladder & riser floor opening propose,tray sizing check and update
PHE
Validate/model Drainage tie-in line upto the risers
Validate/mark the STR opening for Drainage tie-in and share with STR
Obtain feedback from STR and modify the route if required
Ensure the openings are reflected in the STR model
Validate/model Potable water tie-in line upto the Tank
Validate/mark the STR opening for Potable Water tie-in and share with STR
Obtain feedback from STR and modify the route if required
Ensure the openings are reflected in the STR model
Validate/model TSE tie-in line upto the Tank
Validate/mark the STR opening for TSE tie-in and share with STR
Obtain feedback from STR and modify the route if required
Ensure the openings are reflected in the STR model
Validate/model Fire water/Irrigation water breaching inlet line upto the Tank
Validate/mark the STR opening for breaching inlets and share with STR
Obtain feedback from STR and modify the route if required
Validate/model LPG filling line upto the Tank
Validate/mark the STR opening for breaching inlets and share with STR
Obtain feedback from STR and modify the route if required
Ensure the openings are reflected in the STR model

## DD - PHE Detailed Design Update
Fire Fighting Layouts - this activity shall be repeated floor-wise/apartment-wise
Obtain the location of sprinkler heads from the coordinated RCP/wall layouts
Provide clean agent system as per authority requirements
Obtain the pump selection for all fire fighting pumps
Provide the information to electrical team (power) and dimensions to modelers
Engrs to provide mark-ups/information for pipe sizing
Modelers to model all the pipeworks
Modelers to provide check prints to Engrs for review
Engrs to review and provide comments
Modelers to incorporate the comments and finalise the layouts
Firefighting System Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall fire fighting system schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics
Potable Water Supply Layouts - this activity shall be repeated floor-wise/apartment-wise
Obtain the location of all plumbing fixtures from ID for all FOH areas
Obtain the location of all plumbing fixtures from arch for all BOH areas
Carry out the pressure drop calculation until the last fixture and provide PRV's as required
Check pressure across the utility meters (should be within specified pressure limit)
Obtain the pump selection for all domestic water pumps
Provide the information to electrical team (power) and dimensions to modelers
Provide mark-up/information for the modelers to model all the pipe routes
Modelers to model all the pipeworks
Modelers to provide check prints to Engrs for review
Engrs to review and provide comments
Modelers to incorporate the comments and finalise the layouts
Potable Water System Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall potable water system schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics
Drainage Layouts - this activity shall be repeated floor-wise/apartment-wise
Obtain the location of all plumbing fixtures from ID for all FOH areas
Obtain the location of all plumbing fixtures from arch for all BOH areas
Obtain the location of all balcony drains from ID layouts
Review the location of WC's against the location of beams and highlight such issues to ID/arch
Obtain the location of drain points from landscape/pool/water feature consultants
Obtain Piling layout from structure & coordinate the location of sumps & gratings
Review the requirement of floor gratings at Ramp area and inside Pump rooms at Basement & Ground floors
Validate the slope and invert level at the tie-in location
Obtain the pump selection for sump pumps
Provide the information to electrical team (power) and dimensions to modelers
Provide mark-up/information for the modelers to model all the pipe routes
Modelers to model all the pipeworks
Modelers to provide check prints to Engrs for review
Engrs to review and provide comments
Modelers to incorporate the comments and finalise the layouts
Drainage Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall drainage schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics
LPG Layouts - this activity shall be repeated floor-wise/apartment-wise
Obtain the location of all kitchen equipment from ID for all FOH areas
Obtain the location of all kitchen equipment from kitchen consultant for commercial kitchen
Provide mark-up/information for the modelers to model all the pipe routes/PRV's
Modelers to model all the pipeworks
Modelers to provide check prints to Engrs for review
Engrs to review and provide comments
Modelers to incorporate the comments and finalise the layouts
LPG/SNG Schematics - this activity shall commence after completing the layouts
Based on the updates on the layouts, update the overall LPG/SNG schematics
Engr to review the updated schematics and provide their comments
Modelers to incorporate the comments and finalise the schematics

## DD - Secondary Service Routing
Secondary Services Routing | NOT INCLUDED
HVAC | NOT INCLUDED
Carpark Ventilation
Finalise Ventilation Calculations
Validate the location of Make-up & Discharge locations
Validate the size of louvers
Provide Engineering information to BIM team to finalise the ducting from fan room to end distribution
Validate the duct routing from makeup air louver to the last supply air grill as per the revised engineering markup post 100% SD
Validate the duct routing from extract air louver to the last extract air grill as per the revised engineering markup post 100% SD
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
Staircase Pressurization
Finalise Pressurization Calculations
Validate the location of Make-up locations
Validate the size of louvers
Validate/model the duct routing from Fan to shaft
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
Liftwell Pressurization
Finalise Pressurization Calculations
Validate the location of Make-up locations
Validate the size of louvers
Validate/model the duct routing from Fan to shaft
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
Corridor smoke control
Finalise Ventilation Calculations
Validate the location of Make-up & Discharge locations
Validate the size of louvers
Provide Engineering information to BIM team to finalise the ducting from fan room to end distribution
Validate the duct routing from makeup air louver to the last supply air grill as per the revised engineering markup post 100% SD
Validate the duct routing from extract air louver to the last extract air grill as per the revised engineering markup post 100% SD
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
Chilled Water Distribution
Finalise HAP calculation
Provide Engineering information to BIM team to finalise the CHW pipe distribution
Validate/model CHW pipework distribution from ETS to risers and exiting to individual floors
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
General Ventilation
Finalise Ventilation Calculations
Validate the location of Make-up & Discharge locations
Validate the size of louvers
Provide Engineering information to BIM team to finalise the ducting from FAHU's to end distribution
Validate/model all the duct routes
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
AC (for common areas)
Finalise HAP calculation
Provide ENG inputs for modelling equipment/duct routes for each area
Validate/model all the duct routes
Populate the coordination issues in a tracker to ENG for resolution
ENG resolution provided issues highlighted above to BIM team
Electrical
Power Distribution
Populate all the equipment & electrical panels on the basement (coordinate with PHE & HVAC)
Provide SD load schedules to BIM for tray sizing
Provide mark-up for FA/CBS tray route from the riser upto FCC/CBS rooms
Size cable trays and model cable trays for missing loads
Coordinate tray routes with other services while modelling
Review the generator exhaust discharge point & fill point assembly (check the tanker parking)
Validate the routing of Fuel fill line from fill point to Day tank
Assess & Provide if additional shafts required
Provide mark-ups to Arch for incorporating arch model
Verify if this is incorporated in the arch model
PHE
Potable Water Distribution
Finalise water demand calculation
Validate the size of tanks
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Finalise transfer pump & transfer pipe sizing
Obtain pump selections from vendor and provide the information to Elect team (power) and dimensions to modelers
Validate the riser sizes
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Validate/model transfer pipes based on the calculation
Finalise pipe sizing calculation for branch pipes from risers to apartments
Provide mark-ups/information to modelers to validate/model the pipe routes
Eng to review and provide comments
Modelers to update the model based on the comments
Fire Water Distribution
Finalise fire water demand calculation
Validate the size of tanks
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Finalise the riser pipe sizing including low/high zone interconnection
Validate the riser sizes
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Validate/model riser pipes based on the calculation
Provide mark-ups/information to modelers to validate/model the pipe routes
Eng to review and provide comments
Modelers to update the model based on the comments
Drainage
Finalise drainage pipe sizing calculation
Validate the riser sizes
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Validate/model riser pipes based on the calculation
Obtain landscape drain locations from landscape consultant
Validate the slope and invert level at the tie-in location
Provide mark-ups/information to modelers to validate/model the pipe routes
Eng to review and provide comments
Modelers to update the model based on the comments
Rainwater Distribution
Finalise the rainwater calculation for number of outlets & downpipe sizing
Verify if a secondary outlet is required as per client/operator requirement
Validate the riser sizes
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Validate/model riser pipes based on the calculation
Provide mark-ups/information to modelers to validate/model the pipe routes
Eng to review and provide comments
Modelers to update the model based on the comments
LPG/SNG Distribution
Finalise the gas demand & riser pipe sizing calculation
Validate the tank size & riser sizes
Validate the clearances around gas tank where applicable
Provide mark-ups to arch if there are any changes
Follow-up with arch for updated layouts incorporating the changes
Validate/model riser pipes based on the calculation
Provide mark-ups/information to modelers to validate/model the pipe routes
Eng to review and provide comments
Modelers to update the model based on the comments

## DD - STR - Coordination
Coordination (to follow after finalising Primary & Secondary Services Routing) - This coordination shall happen within 2weeks from the DD kick-off | NOT INCLUDED
Wall/Floor Openings
BIM manager to generate clash report for MEP vs STR & MEP vs MEP
BIM manager to produce coordination tracker and assign modelers against the each item
Modelers to complete the coordination issues and validate all the openings (Wall/floor)
Modelers to highlight any missing openings to Engrs
Engr to review and issue a consolidated feedback to arch/str for all the openings
Engrs to obtain the finalised arch/str layout
Equipment weights & plinths
Based on the DD calculations Engrs to obtain equipment selections
Engrs to validate the weight of the equipment & associated plinth sizes
Attic Slabs
Engrs to review any wet areas above electrical/ELV rooms
Engrs to validate all drainage riser diversions
Engrs to validate all Gas riser diversions
Engrs to validate all HVAC riser diversions
Engrs to validate any landlord services within the Retail/F&B spaces
Engrs to validate or modify attic slab extents as per the above and share with arch/str
Engrs to obtain the revised arch/str models for review
Engrs to review and provide feedback to arch/str, if any
Engrs to obtain the finalised arch/str layout